招标说明

说明
CRITO®CrossBoard
连接模块
带框端子 6 - 50 mm² / AWG 10 - AWG 1
3 极

标准
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

认证许可
UL

电气数值
额定电流（IEC）:	125 A
额定电压（IEC）AC:	690 V

额定电流 (UL):	100 A
额定电压 (UL) AC:	600 V
最大电流负载能力 (IEC):	125 A

rated isolation voltage Ui AC:	800 V
最大电压 IEC AC:	800 V
最大电压 IEC DC:	800 V

额定冲击耐受电流 Ipk :	15 kA

SCCR: 100 kA with any DIVQ/7 circuit breaker 100 A / 480 V AC, 65 kA with any DIVQ/7 circuit breaker 100 A / 600 V AC, 100 kA with JDDZ fuse Class J 175 A / 600 V AC 

连接端
6 - 50 mm² / AWG 10 - AWG 1 
feindrähtig, direkt geklemmt oder mit Aderendhülse, 
6 - 35 mm² Rundleiter mehrdrähtig,
(feindrähtig mit Aderendhülse eventuell nicht mit maximalen Querschnitt möglich)

原材料性能
主体:
	耐温性最高 125°C, 
	根据UL 94 有阻燃性, 
	耐蠕变性 CTI 600

其他
direct connection to the CrossBoard, cover included

capable of feeding (up to 125 A) 1 or 2 CrossBoards simultaneously with balanced or unbalanced load on the boards.

can be used without cables as a bridge connection between 2 CrossBoards up to 125 A. Feeding a third CrossBoard with cables is acceptable, but the total current cannot exceed 125 A.

touch-safe

CRITO® unlockable from top or bottom

品牌
维纳尔或同等价值的产品

订货号
01593000A