Text for specification

Description
CRITO®
brace terminal
35 - 150 mm², AWG 2 - 300 MCM,  lam. Cu. 15 - 20 x 5 - 10
30Compact 3P
60Classic

Standards
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Approvals
UL

Electrical data
Rated current (IEC):	275 A
rated voltage (IEC) AC:	690 V

rated current (UL):	285 A
rated voltage (UL) AC:	600 V
current capacity (IEC) max.:	480 A
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1500 V

rated peak withstand current  Ipk max.:	49,8 kA

SCCR:	18 kA

Terminal points
for applications acc. to IEC / EN :
Cu or Al 35 - 150 mm² stranded round cables and stranded sectored cables
Cu also flexible cables, directly or with wire-end ferrule
(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

for applications acc. to UL / CSA :
Cu 35 - 150 mm² / AWG 2 - MCM 300
Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Material properties
Connecting screws:
	Set screw M8, Allan key size 4
Terminal body:
	steel, galvanized and chromized
cable base:
	brass, tin plated

Terminal body: 	galvanised steel, chromited screw: 	hexagon socket screw M8 x 37, cable bed: 	brass, nickel-plated

Miscellaneous 
Terminal with captive clamping screws, conductor can be overlapped.
Indication of nominal cross-section and tightening torque noted on the terminal.
Contact between conductor and busbar via cable bed.

Brand 
Woehner or equivalent

Part No.
01135000