Text for specification

Description
QUADRON®Panel
NH fuse-base 250 A, panel mounting
both sides screw M10
size 1 / 3P, with touch protection

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Electrical data
Rated current (IEC):	250 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	440 V

power dissipation at full load of the item:	16,4 W
rated surge voltage Uimp :	8 kV
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1000 V
short-circuit strength when protected by fuses:	50 kA

for fuse links IEC 60269-2 / DIN VDE 0636-201 size 1 up to 32W power dissipation

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
For safe connection of the leads, the shock protection is split into 6.

Brand 
Woehner or equivalent

Part No.
03763000