Text for specification

Description
EQUES®60Classic
busbar adapter 63 A
for direct starter ABB MS45x, Eaton PKZM4, Siemens S2
55 x 260, with leads AWG 8 (10 mm²)
60Classic

Standards
IEC 61439-1:2011

Approvals
CSA, UL

Electrical data
Rated current (IEC):	63 A
rated voltage (IEC) AC:	690 V

rated current (UL):	65 A
rated voltage (UL) AC:	600 V

power dissipation at full load of the item:	6,9 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV

SCCR: 100 kA with PKZM4 60 A / 480 V AC , 100 kA with MS45x 60 A / 480 V AC , 100 kA with S2 60 A / 480 V AC  

Miscellaneous 
Conductor ends ultrasonically sealed.
Click mechanism when pushing onto the busbar.

Brand 
Woehner or equivalent

Part No.
32460000