Text for specification

Description
EQUES^®60Classic
busbar adapter 32 A
for reversing starter Allen-Bradley 140M-C, 140M-D
54 x 200, with leads AWG 10 (6 mm²)
60Classic

Standards
IEC 61439-1:2011

Approvals
CSA, UL

Electrical data
Rated current (IEC):	25 A
rated voltage (IEC) AC:	690 V

rated current (UL):	30 A
rated voltage (UL) AC:	600 V

power dissipation at full load of the item:	2,4 W

rated isolation voltage U_i AC:	800 V
rated surge voltage U_imp :	6 kV

SCCR: 30 kA with 140M-C, 140M-D 12,5 A / 600 V AC, 65 kA with 140M-C, 140M-D 16 A / 480 V AC, 65 kA with 140M-C, 140M-D 25 A / 480 V AC, 50 kA with 140M-C, 140M-D 32 A / 480 V AC 

Material properties
AWG leads, temperature-resistant up to 105°C

Miscellaneous 
Conductor ends ultrasonically sealed.
Click mechanism when pushing onto the busbar.

Brand 
Woehner or equivalent

Part No.
32534000