Text for specification

Description
EQUES®30Compact
busbar adapter 63 A
1 adjustable mounting rail
54 x 160, with leads AWG 8 (10 mm²)
30Compact 3P

Standards
IEC 61439-1:2011

Approvals
CSA, UL

Electrical data
Rated current (IEC):	63 A
rated voltage (IEC) AC:	690 V

rated current (UL):	65 A
rated voltage (UL) AC:	600 V

power dissipation at full load of the item:	6,9 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV

SCCR: 65 kA with any DIVQ/7 circuit breaker 60 A / 480 V AC , 65 kA with any NKJH/7 Comb. Motor Controller Type E 65 A / 480 V AC 

Material properties
Conductor insulation: 	temperature-resistant up to 105 °C

Miscellaneous 
Conductor ends ultrasonically sealed.
Click mechanism when pushing onto the busbar.

Brand 
Woehner or equivalent

Part No.
32591000