Text for specification

Description
CRITO^®
universal conductor terminal
16 - 120 mm², AWG 6 - 250 MCM
30Compact 3P
60Classic
100Energy
185mm-System
centre feed unit

Standards
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Approvals
CSA, UL

Electrical data
Rated current (IEC):	250 A
rated voltage (IEC) AC:	800 V

rated current (UL):	255 A
rated voltage (UL) AC:	600 V
current capacity (IEC) max.:	440 A
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1500 V

rated peak withstand current  I_pk max.:	62,8 kA

Terminal points
16 - 120 mm² / AWG 4 - MCM 250 
flexible cables, directly or with wire-end ferrule, 
solid round cables, 
lam. Cu 4 x 15.5 x 0,8 or 6 x 15.5 x 0,8 or 10 x 15.5 x 0,8

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
Terminal with integrated holding spring, captive clamping screw and opened terminal space.
Indication of nominal cross-section and tightening torque noted on the terminal.

Brand 
Woehner or equivalent

Part No.
01203000