Text for specification

Description
EQUES®CrossBoard
adapter 16 A
1 adjustable mounting rail, with leads AWG 14 (2.5 mm²)
45 x 160

Standards
IEC 61439-1:2011

Approvals
IEC (CB), UL

Electrical data
Rated current (IEC):	16 A
rated voltage (IEC) AC:	690 V

rated current (UL):	12 A
rated voltage (UL) AC:	600 V

power dissipation at full load of the item:	1,2 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV

SCCR: 50 kA with JDDZ fuse Class CC 20 A / 600 V AC, 65 kA with any NKJH/7 Comb. Motor Controller 12 A / 480 V AC 

Miscellaneous 
Conductor ends ultrasonic compressed.
Click mechanism when pushing onto the CrossBoard®.

Brand 
Woehner or equivalent

Part No.
32668000A