Text for specification

Description
QUADRON 60Classic
NH fuse-switch-disconnector size 00, 160 A
box terminal
suitable for 5-pole system
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), UL, VDE, CCC

Electrical data
rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	440 V

rated current (UL):	160 A
rated voltage (UL) AC:	600 V

AC-22B 500V 160A
AC-22B 690V 125A
AC-23B 500V 125A
AC-23B 400V 160A       

power dissipation at full load of the item:	17,7 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV
max. permitted voltage (IEC) DC:	800 V

SCCR:	100 kA

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.

Bei Dauerbetrieb von mehreren Geräten nebeneinander ist der Bemessungsbelastungsfaktor nach VDE 0660 Teil 500 / EN60439-1, Tabelle 1 zu beachten.

System component: degree of protection IP30 at front as per DIN EN 60529, degree of protection near terminal depends on installation, adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom; the parts under voltage remain shock protected
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two
Busbar supports for flat busbars can be mounted above each other

Brand 
Woehner or equivalent

Part No.
33075000