Text for specification

Description
CAPUS®Panel
PE terminal for SD1-3P switch-disconnector
box terminal 2,5 - 16 mm² / AWG 16 - 6

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
UL

Electrical data
Rated current (IEC):	63 A
rated voltage (IEC) AC:	690 V

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	4 kV
rated making capacity:	2.1 kA

Terminal points
cage clamp connection
wire stripping: 10 mm
min. cross-section: 2.5 mm²
max. cross-section: 16 mm²
cage clamp connection
wire stripping: 10 mm
min. cross-section: 2.5 mm²
max. cross-section: 16 mm²
re: 2.5 - 16 mm²
rm: 16 - 16 mm²
f: 2.5 - 16 mm²
f + AE: 2.5 - 16 mm²
(f + AE may not fit with max. cross-section) 
Md min.: 2.0 Nm
Md max.: 2.0 Nm
Not suitable for aluminium cables !

Brand 
Woehner or equivalent

Part No.
33689000A