Text for specification

Description
universal busbar support
for undrilled flat busbars 30, 40, 50, 60 x 10
100Energy

Standards
IEC 61439-1:2020

Electrical data
rated voltage (IEC) AC:	800 V

rated isolation voltage Ui AC:	1000 V
rated surge voltage Uimp :	8 kV
max. permitted voltage (IEC) DC:	1500 V

short-circuit capacity IEC / EN :
Ipk max. = 85 kA (busbar 60x10, 2 busbar supports in 300 mm distance)
further data see short-circuit diagram

Miscellaneous 
Type tested at 600mm busbar support separation and 60 x 10mm with external screw holes
can also be used as centre support.

Brand 
Woehner or equivalent

Part No.
01479000