Text for specification

Description
AMBUS^®Panel
holder for cylindrical fuses, for semiconductor fuses
14 x 51 / 3P
50 A / 690 V

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), CSA, UL, CCC

Electrical data
Rated current (IEC):	50 A
rated voltage (IEC) AC:	690 V

rated current (UL):	50 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

power dissipation at full load of the item:	2.7 W

rated isolation voltage U_i AC:	800 V
rated surge voltage U_imp :	6 kV

SCCR:	100 kA

for fuse links as per IEC / EN 60269-2 with permitted rated power dissipationsup to max. 5W for gG/gL up to max. 3W for aM for fuse links aR / gR / gRL under operation conditions up to max. 6.5W, for which at least 25mm² leads must be connected

Terminal points
box terminal :
1,5 - 35 mm² / AWG 14 - AWG 2 
flexible cables, directly or with wire-end ferrule
Md 2,5 - 3,0 Nm / 22 - 26 lb.in.

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
large clamping range
 holder for label

Brand 
Woehner or equivalent

Part No.
31280000