Text for specification

Description
AMBUS®60Classic
busbar mounted fuse holder Class J
for fuse links Class J 1 - 30 A (21x57), with LED
3P, complete solution based on busbar adapter
60Classic

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

Approvals
CSA, UL

Electrical data

rated current (UL):	30 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

power dissipation at full load of the item:	3.0 W

SCCR:	100 kA

Terminal points
for applications acc. to IEC / EN :
1 wire : 
Cu 0,75 - 1,0 mm², Md 2,0 - 2,5 Nm / 18 - 22 lb.in.
Cu 1,5 - 50 mm², Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
2 wires (of same cross-section) : 
Cu 0,75 - 1,0 mm², Md 2,0 - 2,5 Nm / 18 - 22 lb.in.
Cu 1,5 - 10 mm², Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E 60°C/75°C
1 wire : 
AWG 18 - AWG 1, Class B, Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
2 wires (of identical cross-section) : 
AWG 18 - AWG 8, Class B, Md 3,5 - 4,0 Nm / 31 - 35 lb.in.

Brand 
Woehner or equivalent

Part No.
31968000