Text for specification

Description
AMBUS®Panel
holder for cylindrical fuses
10x38 / 2P
30 A / 1000 V DC

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Approvals
IEC (CB), CSA, UL, CCC

Electrical data
Rated current (IEC):	30 A
rated voltage (IEC) DC:	1000 V

rated current (UL):	30 A
rated voltage (UL) DC:	1000 V

power dissipation at full load of the item:	0.6 W
rated surge voltage Uimp :	6 kV
max. permitted voltage (IEC) DC:	1000 V

use of fuse links with silver plated caps is recommended

Terminal points
for applications acc. to IEC / EN :
1 wire: 
Cu 0,75 - 25 mm²
2 wires (of same cross-section): 
Cu 0,75 - 10 mm² 
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)
Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E
1 wire: 
AWG 18 - AWG 8, Class B, Md 2,0 -2,5 Nm / 18 - 22 lb.in.
AWG 6 - AWG 4, Class C, Md 2,5 - 3,0 Nm / 22 - 26 lb.in.
2 wires (of identical cross-section): 
AWG 18 - AWG 8, Class B, Md 2,0 - 2,5 Nm / 18 - 22 lb.in. 
AWG 6, Class C, Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

Miscellaneous 
large clamping range
holder for label

Brand 
Woehner or equivalent

Part No.
31974000