Text for specification

Description
CAPUS®Panel
switch-disconnector 3-pole
box terminal 50 - 70 mm² / AWG 1 - 3/0, yellow-red handle
160 A

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
UL

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V

rated current (UL):	125 A
rated voltage (UL) AC:	600 V

AC-23 A (690 V / 125 A)
AC-23 A (500 V / 160 A)
AC-22 A (690 V / 125 A)
AC-22 A (500 V / 160 A)
AC-21 A (690 V / 160 A)

power dissipation at full load of the item:	9.0 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV
rated making capacity:	4.5 kA

Terminal points
für Anwendungen nach IEC / EN :
50 - 70 mm² feindrähtig
Md 6,0 Nm

50 - 70 mm² rund mehrdrähtig
Md 7,2 ....? Nm

50 mm² feindrähtig mit Aderendhülse
6,0 Nm

70 mm² feindrähtig mit Aderendhülse
7,2   ? Nm

für Anwendungen nach UL / CSA :
AWG 6 - 3/0
53,1 lb-in

Miscellaneous 
lockable in 0-position with a padlock (max. 5 mm diameter) 

Brand 
Woehner or equivalent

Part No.
33040000A