Text for specification

Description
CRITO®60Classic
connection terminal plate, 3-pole
95 - 185 mm²
60Classic

Standards
IEC 61439-1:2020
IEC 60999-1:1999
IEC 60999-2:2003

Electrical data
Rated current (IEC):	350 A
rated voltage (IEC) AC:	690 V
current capacity (IEC) max.:	460 A
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1500 V

rated peak withstand current  Ipk max.:	55.8 kA

Terminal points
für Anwendungen nach IEC / EN :
Cu und Al 95 - 185 mm² Rundleiter mehrdrähtig und Sektorleiter mehrdrähtig
Cu auch feindrähtig, direkt geklemmt

for applications acc. to IEC / EN:
Cu or Al 95 - 185mm², round stranded or sector-shaped stranded cables
also fine stranded Cu cables (direct clamping)   

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free

Terminals: 	galvanised steel, chromited screw: 	hexagon socket screw, galvanised, chromited, thrust piece 	brass, nickel-plated

Miscellaneous 
Terminals with captive clamping screws
Conductor can be overlapped
Indication of nominal cross-section and tightening torque noted on the terminals.

Brand 
Woehner or equivalent

Part No.
01199000