Text for specification

Description
CRITO^®
brace terminal
32 x 20
60Classic
100Energy
185mm-System
centre feed unit

Standards
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Approvals
CSA, UL

Electrical data
Rated current (IEC):	550 A
rated voltage (IEC) AC:	690 V

rated current (UL):	800 A
rated voltage (UL) AC:	600 V
current carrying capacity for centre feed:	800 A
current capacity (IEC) max.:	800 A
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1500 V

rated peak withstand current  I_pk max.:	80.9 kA

SCCR:	25 kA

Terminal points
lam. Cu from 3 x 20 x 1 to 10 x 32 x 1

Material properties
Connecting screws:
	Set screw M16, Allan key size 8
Terminal body:
	steel, galvanized and chromized
cable base:
	brass, tin plated

Miscellaneous 
also rigid copper busbars can be connected if they are installed without mechnical tension 

Brand 
Woehner or equivalent

Part No.
01759000