Text for specification

Description
busbar connecting terminal 630 A
150 mm long
60Classic

Standards
IEC 61439-1:2011

Approvals
UL

Electrical data
rated voltage (IEC) AC:	690 V

rated current (UL):	756 A

power dissipation at full load of the item:	2.0 W
current capacity (IEC) max.:	630 A
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1500 V

SCCR: 65 kA in combination with 30x10-L and any DIVQ/7 800 A / 480 V AC 

Material properties
Screws:
	Hexagon screw M12, length across flats 19
Terminal body:
	Cu-ETP R300 (EN 13601), tinned

Terminal body: 	Cu section, nickel-plated, 	for bridging the system separation, screws: 	hexagonal screws M12 with slot, galvanised, chromited

Brand 
Woehner or equivalent

Part No.
01886000