Text for specification

Description
QUADRON®60Classic
NH fuse base 160 A
screw M8
size 00 / 3P
60Classic

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	440 V

power dissipation at full load of the item:	14.0 W
rated surge voltage Uimp :	6 kV
max. permitted voltage (IEC) AC:	800 V
max. permitted voltage (IEC) DC:	800 V
short-circuit strength when protected by fuses:	50 kA

Terminal points
screw connection
M8
screw drive: SW13 
screw connection
M8
screw drive: SW13 
Md min.: 12.0 Nm
Md max.: 14.0 Nm
Not suitable for aluminium cables !

Brand 
Woehner or equivalent

Part No.
03656000