Text for specification

Description
NH busbar mounted fuse base, 400 A
screw
size 2 / 3P
40mm-System

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Electrical data
Rated current (IEC):	400 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	440 V

power dissipation at full load of the item:	56.0 W
rated surge voltage U_imp :	6 kV
max. permitted voltage (IEC) AC:	800 V
max. permitted voltage (IEC) DC:	800 V

for fuse links IEC 60269-2 / DIN VDE 0636-201 size 2 up to 45W power dissipation

Material properties
Main body:
	temperature stability 130°C,
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Connecting screws:
	screw M10, galvanized, chromized

Brand 
Woehner or equivalent

Part No.
03694000