Text for specification

Description
SECUR^®60Classic PowerLiner
busbar mounted switch-disconnector-fuse
for fuses 10x38 IEC 60269-2
3P
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Electrical data
Rated current (IEC):	32 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	110 V

AC-23A (400 V)
AC-22A (690 V) 

power dissipation at full load of the item:	5.3 W

rated isolation voltage U_i AC:	500 V
rated surge voltage U_imp :	6 kV
max. permitted voltage (IEC) AC:	725 V

for fuse links gG and aM as per IEC / EN 60269-2

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

Material properties
Body:
	temperature stability 140°C,
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 225,
	silicon-free, halogen-free
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Fuse-carrier:
	temperature stability 150°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 125,
	halogen-free
Cover:
	temperature stability 125°C,
	fire behaviour UL 94 HB,
	creepage resistance CTI 200,
	halogen-free 
Connecting screws:
	screw +/- (PZ2), galvanized, chromized 

Brand 
Woehner or equivalent

Part No.
31232000