Text for specification

Description
CUSTO®60Classic
D0-fuse base, busbar mounted, 36mm
E 18 / 63 A
touch protected
60Classic

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-3:2010 + A1:2013 + A2:2019

Approvals
VDE

Electrical data
Rated current (IEC):	63 A
rated voltage (IEC) AC:	400 V
rated voltage (IEC) DC:	250 V

power dissipation at full load of the item:	5.9 W
rated surge voltage Uimp :	6 kV
max. permitted voltage (IEC) AC:	440 V
max. permitted voltage (IEC) DC:	262 V
short-circuit strength when protected by fuses:	50 kA

Direct contact of the fuse links on the busbar

It can be used for branch circuits of the busbar system. The application as feeder of a busbars system is not accepted. 

Brand 
Woehner or equivalent

Part No.
31936000