Text for specification

Description
EQUES^®60Classic
busbar adapter 250 A, 3-pole
105 x 190
60Classic

Standards
IEC 61439-1:2011

Approvals
CSA, UL

Electrical data
Rated current (IEC):	250 A
rated voltage (IEC) AC:	690 V

rated current (UL):	250 A
rated voltage (UL) AC:	600 V

power dissipation at full load of the item:	15.6 W

rated isolation voltage U_i AC:	800 V
rated surge voltage U_imp :	6 kV

SCCR: 50 kA with NSX250 / 600 V  AC, max. busbar support distance 400 mm, 25 kA with NSX250 / 600 V  AC, 65 kA with NSX250 / 480 V AC 

Brand 
Woehner or equivalent

Part No.
32156000