Text for specification

Description
QUADRON^®Panel
NH fuse switch-discon. size 2, 400 A, panel mounting
screw M10

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
CCC

Electrical data
Rated current (IEC):	400 A
rated voltage (IEC) AC:	690 V

rated current (UL):	400 A
rated voltage (UL) AC:	600 V

AC-23B (400V)
AC-22B (690V)
AC-21B (690V)
AC-20B (1000V) at pollution degree 2

visible information required if used at more than 690V AC: do not switch under load

DC specifications: 2 current paths (L1,L3) in series
DC-22B (440V)
DC-21B (440V)
DC-20B (1000V) at pollution degree 2

visible information required if used at more than 440V DC: do not switch under load

rated isolation voltage U_i AC:	1000 V
rated surge voltage U_imp :	12 kV

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 

Miscellaneous 
Disconnectors are equipped with arc chambers.
The shock protection is split into 2 for safe connection of the conductors.
Self-closing inspection holes are available in the cover.

Brand 
Woehner or equivalent

Part No.
33018000AC