Text for specification

Description
QUADRON®60Classic Speed
switch disconnector with fuses, 3-pole
box terminal, connection top, for door coupling rotary handle
size 00
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Electrical data
Rated current (IEC):	125 A
rated voltage (IEC) AC:	690 V

AC-23B (690V/125A)
AC-23A (500V/125A)
AC-22A (690V/125A)

AC20B (800V)
visible information required: do not switch under load

DC specifications: 2 current paths (L1,L3) in series
DC-22B (220V/125A)

DC-20B (800V) at pollution degree 3
visible information required: do not switch under load

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	8 kV

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

When several devices are used side-by-side in continuous operation, the rated load factor specified in VDE 0660 Part 500 / EN 60 439-1, Table 1, must be observed.

System component: degree of protection IP20 at front as per DIN EN 60529, degree of protection near terminal depends on installation; shock protection as per DIN EN 50274

adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

Miscellaneous 
With spring-controlled switch mechanism for frequent switching as per utilisation category "A"
FLAG indicator shows the switch setting
Fuses can be changed safely and without tools thanks to double-breaking main contacts
Additional visible separating section by removing the cover incl. fuses
Can be used as mains disconnector as per IEC / EN 60204-1 (main switch)
Also as an Emergency Off switch in combination with the red-yellow door coupling twist handle
Main switch and Emergency Off switch only in combination with AC-23A/B

CrossLink® adapter technology
Simple and safe clicking into place and making contact
Busbar supports can be mounted above each other for flat busbars
Compact dimensions (106mm wide)

Switches can be installed 90° left/right horizontal, always with the same switch lug position

Brand 
Woehner or equivalent

Part No.
33504000