Text for specification

Description
connecting set 2500 A (3-pole)
200 mm, flexible longitudinal connection
60Classic
185mm-System

Standards
IEC 61439-1:2011

Electrical data
rated voltage (IEC) AC:	690 V

power dissipation at full load of the item:	56.2 W
current capacity (IEC) max.:	2,500 A
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1500 V

rated peak withstand current  Ipk max.:	91.7 kA

Brand 
Woehner or equivalent

Part No.
01295000