Text for specification

Description
CRITO®CrossBoard
connection module
with box terminals 6 - 50 mm² / AWG 10 - AWG 1
3-pole

Standards
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Approvals
UL

Electrical data
Rated current (IEC):	125 A
rated voltage (IEC) AC:	690 V

rated current (UL):	100 A
rated voltage (UL) AC:	600 V
current capacity (IEC) max.:	125 A

rated isolation voltage Ui AC:	800 V
max. permitted voltage (IEC) AC:	800 V
max. permitted voltage (IEC) DC:	800 V

rated peak withstand current  Ipk max.:	15 kA

SCCR: 100 kA with any DIVQ/7 circuit breaker 100 A / 480 V AC, 65 kA with any DIVQ/7 circuit breaker 100 A / 600 V AC, 100 kA with JDDZ fuse Class J 175 A / 600 V AC 

Terminal points
6 - 50 mm² / AWG 10 - AWG 1 
feindrähtig, direkt geklemmt oder mit Aderendhülse, 
6 - 35 mm² Rundleiter mehrdrähtig,
(feindrähtig mit Aderendhülse eventuell nicht mit maximalen Querschnitt möglich) 

Miscellaneous 
direct connection to the CrossBoard, cover included

capable of feeding (up to 125 A) 1 or 2 CrossBoards simultaneously with balanced or unbalanced load on the boards.

can be used without cables as a bridge connection between 2 CrossBoards up to 125 A. Feeding a third CrossBoard with cables is acceptable, but the total current cannot exceed 125 A.

touch-safe

CRITO® unlockable from top or bottom

Brand 
Woehner or equivalent

Part No.
01593000A