Text for specification

Description
CRITO®60Classic
connection terminal plate, 3-pole
lam. Cu. 20 - 32 x 3 - 15
60Classic

Standards
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Electrical data
Rated current (IEC):	550 A
rated voltage (IEC) AC:	690 V
current capacity (IEC) max.:	800 A
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1500 V

rated peak withstand current  Ipk max.:	63.1 kA

Terminal points
lam. Cu from 3 x 20 x 1 to 10 x 32 x 1

Miscellaneous 
also rigid copper busbars can be connected if they are installed without mechnical tension 

Brand 
Woehner or equivalent

Part No.
01753000