Text for specification

Description
EQUES®60Classic
busbar adapter 590 A, 3-pole
140 x 300
60Classic

Standards
IEC 61439-1:2011

Approvals
CSA, UL

Electrical data
Rated current (IEC):	590 A
rated voltage (IEC) AC:	690 V

rated current (UL):	630 A
rated voltage (UL) AC:	600 V

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV

SCCR: 150 kA with 3VA63, 3VA64 / 480 V AC, 200 kA with  3VA53, 3VA54, 3VA63, 3VA64 / 240 V AC, 35 kA with  3VA53, 3VA54 / 600 V AC, 50 kA with 3VA64 / 600 V AC, 100 kA with 3VA53, 3VA54 / 480 V AC 

Brand 
Woehner or equivalent

Part No.
32031000A