Text for specification

Description
EQUES^®CrossBoard
adapter 160 A
90 x 160

Standards
IEC 61439-1:2011

Approvals
UL

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V

rated current (UL):	100 A
rated voltage (UL) AC:	600 V

power dissipation at full load of the item:	9.8 W

rated isolation voltage U_i AC:	800 V
rated surge voltage U_imp :	6 kV

SCCR: 100 kA with any DIVQ/7 circuit breaker 125 A / 480 V AC, 42 kA with any DIVQ/7 circuit breaker 125 A / 600 V AC 

Folgende notwendige Reduktionen wurden durch Prüfungen ermittelt:
Leistungsschalter Siemens: 
Siemens 3VA11, Leitungsabgang unten: 144 A
Siemens 3VA11, Leitungsabgang oben: 136 A
Siemens 3VA51, Leitungsabgang unten: 125A
Siemens 3VA51, Leitungsabgang oben: 112 A

Miscellaneous 
Capable of feeding and bridging two CrossBoards simultaneously.

Brand 
Woehner or equivalent

Part No.
32690000A