Text for specification

Description
QUADRON®Panel
holder for cylindrical fuses
Class J / 3P, terminal 300 mm²
400 A / 600 V (54x181)

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

Approvals
CSA, UL

Electrical data

rated current (UL):	400 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

power dissipation at full load of the item:	14.8 W

SCCR:	200 kA

for Class J fuses 225 - 400A as per UL 248-8 (54x181)

Terminal points
tunnel terminal with hole of 23,0 mm diameter

acc. to IEC / EN :
16 - 240 (300) mm²
flexible cables, directly or with wire-end ferrule, 
solid and stranded round cables, 
Md 38 - 40 Nm

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

acc. to UL :
AWG 4 - MCM 600
stranded cables Class B acc. to UL 486E
336 - 355 lb.in.

Brand 
Woehner or equivalent

Part No.
33308000