Text for specification

Description
NH fuse switch-disconnector size 00, 160 A
screw M8
with electronic fuse monitoring
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
CCC

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	250 V

AC-22B (500 V)

power dissipation at full load of the item:	17.7 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV
max. permitted voltage (IEC) AC:	725 V
max. permitted voltage (IEC) DC:	262 V

In accordance with the specified AC and DC switching properties and in consideration of the overload conditions, certain distances to earthed metal parts are to be adhered to. Please ask Wöhner for details.
When used as a disconnector, the spacings can be ignored.

When several devices are used side-by-side in continuous operation, the rated load factor specified in VDE 0660 Part 500 / EN 60 439-1, Table 1, must be observed.

System component: degree of protection IP30 at front as per DIN EN 60529, degree of protection near terminal depends on installation
adapter module: degree of protection IP20 at front as per DIN EN 60529 (finger-safe)

fuse monitoring:
without auxiliary energy
current may flow in and direction
one opener and one closer, potential-free
AC 5A/250V
DC 5A/30V
DC 0.2A/250V
red flashing indicator in case of defective fuse
automatic reset when replacing fuse
for further information, see assembly manual

Brand 
Woehner or equivalent

Part No.
33394000AC