Text for specification

Description
AMBUS®Panel
N module
10 x 38 / N
32 A / 690 V

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Electrical data
Rated current (IEC):	32 A
rated voltage (IEC) AC:	690 V

rated current (UL):	30 A

power dissipation at full load of the item:	0,3 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV

Terminal points
for applications acc. to IEC / EN :
1 wire: 
Cu 0,75 - 25 mm²
2 wires (of same cross-section): 
Cu 0,75 - 10 mm² 
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)
Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E
1 wire: 
AWG 18 - AWG 8, Class B, Md 2,0 -2,5 Nm / 18 - 22 lb.in.
AWG 6 - AWG 4, Class C, Md 2,5 - 3,0 Nm / 22 - 26 lb.in.
2 wires (of identical cross-section): 
AWG 18 - AWG 8, Class B, Md 2,0 - 2,5 Nm / 18 - 22 lb.in. 
AWG 6, Class C, Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Fuse-carrier:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Connecting screws:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
large clamping range
holder for label

Brand 
Woehner or equivalent

Part No.
31258000