Text for specification

Description
QUADRON^®Panel
NH fuse switch-disconnector size 00, 160 A, panel mounting
screw M8, with short protection cover

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), UL, CCC

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	440 V

rated current (UL):	160 A
rated voltage (UL) AC:	600 V

AC-23B (400V)
AC-23B (500V/125A)
AC-22B (690V)
AC-21B (690V)
AC-20B (1000V) at pollution degree 2

visible information required if used at more than 690V AC: do not switch under load

DC specifications: 2 current paths (L1,L3) in series
DC-22B (220V)
DC-22B (440V/125A)
DC-21B (440V)
DC-20B (1000V) at pollution degree 2

visible information required if used at more than 440V DC: do not switch under load

power dissipation at full load of the item:	7,0 W

rated isolation voltage U_i AC:	800 V
rated surge voltage U_imp :	6 kV
max. permitted voltage (IEC) DC:	800 V

SCCR:	100 kA

In accordance with the specified AC and DC switching properties and in consideration of the overload conditions, certain distances to earthed metal parts are to be adhered to. Further information on request.
When used as a disconnector, the spacings can be ignored.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Terminal points
Accessories:
Clamp connection:  Cu 1.5-70mm² s(r), f+AE; lam. Cu 12x1-10; 3Nm torque
single wedge clamp terminal: Cu, Al* 16-70mm² s(r), s(s), f+AE; 3Nm torque
tunnel terminal 3x Cu 1.5-16mm² s(r), f+AE; 3Nm torque

*Connections not maintenance-free if aluminium conductors are used.

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Contacts:
	spring-loaded copper contacts, silver plated 

Miscellaneous 
For safe connection of the leads, the shock protection is split into 2. Self-closing inspection holes are available in the cover.

Brand 
Woehner or equivalent

Part No.
33222000