Text for specification

Description
TRITON^®Panel
D0 fuse base, panel-mounting
E 14 / 16 A / 3P
touch protected acc. to DGUV V3

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-3:2010 + A1:2013 + A2:2019

Approvals
CCC

Electrical data
Rated current (IEC):	16 A
rated voltage (IEC) AC:	400 V
rated voltage (IEC) DC:	250 V

power dissipation at full load of the item:	1,2 W
rated surge voltage U_imp :	6 kV
max. permitted voltage (IEC) AC:	440 V
max. permitted voltage (IEC) DC:	262 V
short-circuit strength when protected by fuses:	50 kA

The feed direction marked on the product must be strictly observed. 

Terminal points
box terminal :
1,5 - 35 mm² flexible cables, directly or with wire-end ferrule,
1,5 - 10 mm² solid round cables
Md 4,0 Nm

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
large clamping range, holder for label

Brand 
Woehner or equivalent

Part No.
31288000