Text for specification

Description
QUADRON®Panel Speed
switch-disconnector 3-pole
box terminal
160 A

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V

AC-23B (690V/125A), AC-23A (500V/125A), AC-22A (690V/160A)

DC specifications: 2 current paths (L1,L3) in series
DC-22B (220V/125A)

3 current paths (L1, L2, L3) in series
DC-22B (440V/63A) 

power dissipation at full load of the item:	36,0 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	8 kV

rated short-circuit making capacity 7kA (690V AC) cond. rated short-circuit current 50kA (fuses gL/gG size 00 125A-690V AC)

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

When several devices are used side-by-side in continuous operation, the rated load factor specified in VDE 0660 Part 500 / EN 60 439-1, Table 1, must be observed.

System component: degree of protection IP20 at front as per DIN EN 60529, dependent upon installation in the connection area; shock protection to DIN EN 50274

Terminal points
Box terminal:
1.5 -70mm² flexible cables, directly or with wire-end ferrules*, depending on contour of the insulated lead 95mm² could be connectable 
1.5 - 10mm² solid round
16 - 70mm² stranded round 
2x10mm², 2x16mm² and 2x25mm² flexible with wire-end ferrules, identical cables placed side by side, crimping square 
2x10 - 2x35mm² flexible, identical cables placed side by side square

lam. Cu. 9-13 mm wide 
Terminal space 13mm x 13mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
With spring-controlled switch mechanism for frequent switching as per utilisation category &quot;A&quot;
Lockable in neutral position with up to 3 padlocks
FLAG indicator shows the switch setting
double-breaking main contacts
Can be used as a mains disconnector as per IEC / EN 60204-1 (main switch)
Main switch only in combination with AC-23A/B
AC-23B (690V/125A), AC-23A (500V/125A)

Compact dimensions (106mm wide)

Brand 
Woehner or equivalent

Part No.
33542000