Text for specification

Description
CRITO®30Compact
Connection terminal plate, 3 pole
6 - 50 mm², AWG 10 - 2/0, lam. Cu. 7 - 9 x 4 - 10
30Compact 3P

Standards
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Approvals
UL

Electrical data
Rated current (IEC):	175 A
rated voltage (IEC) AC:	690 V

rated current (UL):	175 A
rated voltage (UL) AC:	600 V
current capacity (IEC) max.:	300 A
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1500 V

rated peak withstand current  Ipk max.:	40.5 kA

Terminal points
6 - 50 (70) mm² / AWG 10 - AWG 2/0 
flexible cables, directly or with wire-end ferrule, 
stranded round cables 
lam. Cu 7x4 - 9x6
Md 8-10 Nm / 71 lb-in

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200

Miscellaneous 
Terminals can be removed for connection of uncut conductors

Brand 
Woehner or equivalent

Part No.
01401000