Text for specification

Description
SECUR®Panel
holder for cylindrical fuses
10 x 85 / 1P
32 A, 1500 V DC

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Approvals
UL

Electrical data
Rated current (IEC):	32 A
rated voltage (IEC) AC:	1000 V
rated voltage (IEC) DC:	1500 V

rated current (UL):	30 A
rated voltage (UL) DC:	1500 V

power dissipation at full load of the item:	0.3 W
rated surge voltage Uimp :	8 kV

SCCR:	15 kA

for fuse links 10x85 or 14x85 as per IEC 60269-2, -4, -6
with permitted rated power dissipations up to max. 6.0W

Terminal points
Box terminal

for applications acc. to IEC / EN :
1 wire: 
Cu 0,75 - 25 mm²
2 wires (of same cross-section): 
Cu 0,75 - 10 mm² 
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)
Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

for applications acc. to UL  :
only stranded Cu cables acc. to UL 486E
1 wire: 
AWG 18 - AWG 4
2 wires (of identical cross-section): 
AWG 18 - AWG 6
Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Fuse-carrier:
	temperature stability 140°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Connecting screws:
	screw +/- (PZ2), galvanized, chromized 
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200

Miscellaneous 
easy replacement of the fuse-link
front degree of protection IP20 always guaranteed

Brand 
Woehner or equivalent

Part No.
31555000