Text for specification

Description
CrossBoard®
basic system 125 A
3-pole
225 mm long, touch-safe protected

Standards
IEC 61439-1:2020

Approvals
IEC (CB), UL

Electrical data
rated current (IEC):	125 A
rated voltage (IEC) AC:	690 V

rated current (UL):	100 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

power dissipation at full load of the item:	5.3 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV
max. permitted voltage (IEC) DC:	800 V

rated peak withstand current  Ipk max.:	25 kA

SCCR: 65 kA with any DIVQ/7 circuit breaker 100 A / 600 V AC, 100 kA with any DIVQ/7 circuit breaker 100 A / 480 V AC, 100 kA with JDDZ fuse Class J 175 A / 600 V AC 

Miscellaneous 
all-round touch-safe protected busbar system up to 125 A
mounting to DIN rails with no tools
simple screwing-on to mounting plates
completely pre-assembled and ready to use

Brand 
Woehner or equivalent

Part No.
11225000A