Text for specification

Description
SECUR®60Classic PowerLiner
D0 busbar mounted switch-disconnector-fuse
for fuse links D01 and D02
E18 / 63 A / 3P
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
VDE, CCC

Electrical data
Rated current (IEC):	63 A
rated voltage (IEC) AC:	400 V
rated voltage (IEC) DC:	110 V

AC-23A (400 V)

DC-21B (48V) 1 pole
DC-21B (110V) 2 poles

power dissipation at full load of the item:	10.5 W

rated isolation voltage Ui AC:	500 V
rated surge voltage Uimp :	6 kV

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3
utilisation category as per VDE 0638: AC22

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

Terminal points
frame terminal:
Cu 1,5 - 6 mm² round solid
Cu 1,5 - 16 mm² flexible with or without ferrule

Brand 
Woehner or equivalent

Part No.
31158000