Text for specification

Description
SECUR®60Classic EasyLiner
D0 switch-disconnector-fuse, for 5-pole busbar system
for D01 and D02 fuses
E18 / 63 A / 3P
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), VDE, CCC

Electrical data
Rated current (IEC):	63 A
rated voltage (IEC) AC:	400 V

AC-22B (400 V)

power dissipation at full load of the item:	7.0 W

rated isolation voltage Ui AC:	500 V
rated surge voltage Uimp :	6 kV

reduction factor at ambient temperature:
 35°C     1,0
 45°C     0,9
 55°C     0,8

for fuse links and gauge elements acc. to IEC / HD 60269-3

 use of D02 fuse links with silver plated caps is recommended

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

Terminal points
1,5 - 16 mm² round stranded and flexible without wire-end ferrule
1,5 - 16 mm²  flexible with wire-end ferrule*
1,5 - 10 mm²  flexible with wire-end ferrule
1,5 - 10 mm² round solid

* 16 mm² prepared with crimping tool PZ 16 (Weidmüller) or
with jointing clamp Crimpfox 25R (Phoenix Contact)

the connecting wires can be placed at the side :
up to 6mm² without side module
up to 10mm² when using  the side module

Miscellaneous 
spring terminal enables connection without tools (at first installation)

Brand 
Woehner or equivalent

Part No.
31578000B