Text for specification

Description
EQUES®60Classic
busbar adapter 32 A
45 x 260, with plug-in connection 3RV29 (Siemens)
60Classic

Standards
IEC 61439-1:2020

Approvals
CSA, UL

Electrical data
Rated current (IEC):	32 A
rated voltage (IEC) AC:	690 V

rated current (UL):	32 A
rated voltage (UL) AC:	600 V

power dissipation at full load of the item:	2.5 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV

SCCR: 30 kA with 3RV2.1/2.2 up to 12,5 A in combination with upstream JDDZ fuse Class J 100 A/ 600 V AC, 65 kA with 3RV2.1/2.2 up to 25 A / 480 V AC, 65 kA with 3RV2.1/2.2 up to 16 A / 480 V AC, 50 kA with 3RV2.1/2.2 up to 32 A in combination with upstream JDDZ fuse Class J 100 A/ 480 V AC 

Miscellaneous 
Werkzeuglose Kontaktierung zum Schaltgerät mit Stecker 3RV29
Rastmechanismus beim Aufschieben auf die Sammelschiene. 

Brand 
Woehner or equivalent

Part No.
32037000A