Text for specification

Description
QUADRON^®60Classic
NH fuse switch-disconnector size 3, 630 A
screw M12
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), UL, CCC

Electrical data
Rated current (IEC):	630 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	250 V

rated current (UL):	600 A
rated voltage (UL) AC:	600 V

AC-23B (400V)
AC-22B (690V)
AC-21B (690V)

DC specifications: 2 current paths (L1,L3) in series
DC-22B (250V)

power dissipation at full load of the item:	60.0 W

rated isolation voltage U_i AC:	800 V
rated surge voltage U_imp :	6 kV
max. permitted voltage (IEC) AC:	725 V
max. permitted voltage (IEC) DC:	262 V

SCCR:	100 kA

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.
Bei Verwendung als Trennschalter ist die Einhaltung der Abstände nicht erforderlich.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

fuse monitoring:
rated operating voltage
AC 24-690V, DC 24-250V
potential-free opener and closer:
AC-15 24V/2A, (230V* 0.5A)
DC-13 24V/1A, 60V 0.15A

*pollution degree 2, surge category II
auxiliary energy not required,
for further information, see assembly manual

Terminal points
Accessories:
Clamp connection:  Cu 150-300mm² s(r), f+AE; lam. Cu 25x1-13; 6-8Nm torque
single wedge clamp terminal: Cu, Al* 150-300mm² s(r), s(s), f, f+AE; 6-8Nm torque

*Connections are not maintenance-free if aluminium conductors are used.

Miscellaneous 
Disconnectors are equipped with arc chambers.
The shock protection is split into 2 for safe connection of the conductors.

Brand 
Woehner or equivalent

Part No.
33162000