Text for specification

Description
QUADRON®Panel
NH fuse switch-disconnector size 00, 160 A, panel mounting
clamp 70 mm², with short protection cover

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), UL, CCC

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	440 V

rated current (UL):	160 A
rated voltage (UL) AC:	600 V

AC-23B (400V)
AC-23B (500V/125A)
AC-22B (690V)
AC-21B (690V)
AC-20B (1000V) at pollution degree 2

visible information required if used at more than 690V AC: do not switch under load

DC specifications: 2 current paths (L1,L3) in series
DC-22B (220V)
DC-22B (440V/125A)
DC-21B (440V)
DC-20B (1000V) at pollution degree 2

visible information required if used at more than 440V DC: do not switch under load

power dissipation at full load of the item:	7.0 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV
max. permitted voltage (IEC) DC:	800 V

SCCR:	100 kA

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.
Bei Verwendung als Trennschalter ist die Einhaltung der Abstände nicht erforderlich.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Terminal points
clamp-type terminals : 
1.5 - 70 mm² 
flexible cables with wire-end ferrule, 
stranded round cables, 
lam. Cu max. 12 mm wide, max. 10 mm thick
Md 3 Nm

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
For safe connection of the leads, the shock protection is split into 2.

Brand 
Woehner or equivalent

Part No.
33221000