Text for specification

Description
QUADRON®Panel
NH fuse-base 250 A, panel mounting, for PV
incoming connection screw M10, outgoing connection to busbar 2x 30 x 10, for integrated mounting of CTs type LEM HTA
size 1XL / 1P, with touch protection

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Electrical data
Rated current (IEC):	250 A
rated voltage (IEC) AC:	1000 V
rated voltage (IEC) DC:	1500 V

power dissipation at full load of the item:	5.5 W
rated surge voltage Uimp :	6 kV
short-circuit strength when protected by fuses:	50 kA

for fuse links IEC 60269-6

Terminal points
Connection screws for busbars: Hexagonal screw M10, length across flats 16, tightening torque 30Nm
connection width 25mm 
fastening to mounting plate: 2x 10.5mm hole, intended for hexagonal screw M10, tightening torque 5Nm

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Connecting screws:
	screw M10, galvanized, chromized
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
For one or two internal busbars 30x10mm.
Busbar fully shock protected by the contact cover.
The shock protection is split into 2.

Brand 
Woehner or equivalent

Part No.
03288000