Text for specification

Description
universal busbar support
 
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Standards
IEC 61439-1:2020

Approvals
UL

Electrical data
rated voltage (IEC) AC:	800 V
rated voltage (UL) AC:	1000 V
rated voltage (UL) DC:	1000 V

rated isolation voltage Ui AC:	1000 V
rated surge voltage Uimp :	8 kV
max. permitted voltage (IEC) DC:	1500 V

rated peak withstand current  Ipk max.:	106 kA

short-circuit capacity IEC / EN :
Ipk max. = 106 kA (busbars 120x10, 2 busbar supports in 550 mm distance)
go to calculation for  3-pole system (IEC) 

Brand 
Woehner or equivalent

Part No.
01430000A