Text for specification

Description
SECUR®60Classic PowerLiner
D0 busbar mounted switch-disconnector-fuse
for D01 and D02 fuses, with LED
E18 / 63 A / 3P
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
VDE, CCC

Electrical data
Rated current (IEC):	63 A
rated voltage (IEC) AC:	400 V
rated voltage (IEC) DC:	110 V

AC-23A (400 V)

DC-21B (48V) 1 pole
DC-21B (110V) 2 poles

power dissipation at full load of the item:	10.5 W

rated isolation voltage Ui AC:	500 V
rated surge voltage Uimp :	6 kV

LED indicates blown fuse, operating range: 110 - 400 V AC / DC

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3
utilisation category as per VDE 0638: AC22

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard.

There is a transfer of the potential from the busbars, through the LED units, to the terminals  when the fuse links are removed and the switching mechanismn is closed. 

Material properties
Body:
	temperature stability 140°C,
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 225,
	silicon-free, halogen-free
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Fuse-carrier:
	temperature stability 150°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 125,
	halogen-free
Cover:
	temperature stability 125°C,
	fire behaviour UL 94 HB,
	creepage resistance CTI 200,
	halogen-free 
Connecting screws:
	screw +/- (PZ2), galvanized, chromized 

Brand 
Woehner or equivalent

Part No.
31525000