Text for specification

Description
CAPUS^®Panel
switch disconnector with fuses, 3-pole
screw M12, graphite-grey handle
size 3

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB)

Electrical data
Rated current (IEC):	630 A
rated voltage (IEC) AC:	690 V

AC-23B (690V)
AC-22B (690V)
AC-21B (690V)

power dissipation at full load of the item:	268.0 W

rated isolation voltage U_i AC:	1000 V
rated surge voltage U_imp :	12 kV

Mechanical lifespan (switching operations) 4000

conv. therm. current in housing
630 A, horizontal installation (adjacent poles) encapsulated 756 x 378 x 428 mm
470 A, vertical installation (poles beneath each other) encapsulated 600 x 600 x 400mm

Shock protection at front with terminal space cover IP20

for fuse links DIN 43620 size 3 up to 48W power dissipation

Terminal points
screw M12 :
Md 36 - 44 Nm

Miscellaneous 
double-breaking main contacts,
visible separation sections,
user-independent switching,
voltage-free exchange of fuses
assembly and connection material contained in scope of delivery.

Brand 
Woehner or equivalent

Part No.
33340000