Text for specification

Description
CRITO®185Power
connection module with cover
für Kabeldirektanschluss, Rahmenklemme Cu 300 mm² / Al 240 mm²
angled
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Standards
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Electrical data
Rated current (IEC):	500 A
rated voltage (IEC) AC:	690 V
current capacity (IEC) max.:	630 A
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1500 V

rated peak withstand current  Ipk max.:	50 kA

Terminal points
Cu, Al: 70 - 240 mm² stranded round
Cu, Al: 70 - 240 mm² stranded sectored
Cu, Al: 70 - 240 mm² solid sectored
Cu: 300 mm² stranded round
Cu: 300 mm² stranded sectored
Cu: 70 - 185 mm² flexible with wire-end ferrules

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Brand 
Woehner or equivalent

Part No.
01423000A