Text for specification

Description
QUADRON®Panel
NH fuse-base 160 A
both sides screw M8
size 00 / 3P, with long touch protection cover

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	440 V

power dissipation at full load of the item:	12.5 W
rated surge voltage Uimp :	6 kV
max. permitted voltage (IEC) AC:	800 V
max. permitted voltage (IEC) DC:	800 V
short-circuit strength when protected by fuses:	50 kA

for fuse links IEC 60269-2 / DIN VDE 0636-201 size 00 up to 12W power dissipation

Brand 
Woehner or equivalent

Part No.
03212000